## Slide 1
Waste heat opportunities, monitoring, and applied integration scenario
Unit 5
www.repowerregions.eu
Module 4. Integrating with District ​& Renewable Heat

## Slide 2
01
What is recoverable surplus heat?
02
Screening a potential heat source
03
Industrial and urban heat sources
04
Integration arrangements
05
Monitoring and performance evidence
06
Risks, responsibilities and commercial interfaces
07
Applied integration scenario and conclusions
TABLE OF CONTENTS

## Slide 3
Learning Objective
By the end of this session, learners should be able to:
identify common industrial and urban surplus-heat sources;
screen a potential source using temperature, capacity, timing, distance and reliability;
distinguish between direct use, heat-pump boosting, return-line use and storage;
identify the main monitoring points and operating risks;
recommend whether a source should be investigated further, rejected or escalated for detailed study.

## Slide 4
Why recover heat that is already available?
District-heating systems can use heat that would otherwise be released to:
air;
water;
cooling towers;
wastewater;
exhaust or ventilation air.
Recovering suitable surplus heat can:
displace higher-carbon heat production;
reduce local heat rejection;
improve energy-system efficiency;
support lower-temperature heat networks;
diversify the network’s heat-source mix.
Recovery should not reduce incentives to improve the source process itself.
Recovered heat is not automatically renewable, low-carbon or low-cost.
Notes: The European Commission proposed a strategy to make heating and cooling in the EU more efficient and sustainable. This strategy highlights the capacity of district energy systems to integrate the increasing share of renewable electricity generation and to replace fossil fuels with waste heat and cold from industrial processes, waste-to-energy and renewable energy sources such as geothermal, biomass, solar thermal.

## Slide 5
Waste heat, surplus heat and recovered heat
Surplus heat
Heat leaving a process that is not currently used by that process.
Waste heat
A common term for heat that would otherwise be rejected to the environment.
Recovered heat
Surplus heat that is captured and put to a useful purpose.
Screening principle
Use the heat hierarchy:
prevent unnecessary heat generation;
improve the source process;
reuse heat on-site where practical;
recover remaining heat for nearby users or a heat network.
Heat export should use genuinely available surplus heat—not create additional energy consumption merely to produce saleable heat.

## Slide 6
Six questions for screening a heat source
Temperature Is the source hot enough for direct use (through heat exchanger with no temperature boosting), or is a heat pump required?
Capacity How much technically recoverable power and usable annual energy are available under normal and part-load conditions?
Availability When is the heat available, and does that match network demand?
Location What pipe route, distance and planning constraints apply?
Reliability and lifetime Will the process operate consistently for the investment period?
Carbon and system benefit What existing heat production will actually be displaced?

## Slide 7
Does the source temperature match the network?
Source temperature high enough
If the source temperature is high enough (e.g., industrial flue gases or waste-to-energy), it can be transferred to the network through a heat exchanger.
Source temperature too low
Urban sources like data centers or sewage systems often provide low-grade heat. When the source temperature is lower than the network's required flow, large-scale heat pumps are commonly required to raise the temperature to a usable level.

## Slide 8
Where can recovered heat enter the system?
Supply-line integration
Used when the recovered-heat system can deliver the required supply temperature.
Possible benefit: directly displaces central heat production.
Important checks:
temperature control;
pressure compatibility;
network flow direction;
plant coordination.
Return-line integration
May be used when the source can raise return-water temperature but cannot meet supply temperature.
Possible benefit: preheats water before central generation.
Possible disadvantage:
raises plant return temperature;
may reduce condensing, heat-pump or CHP performance;
may reduce network ΔT.
Return-line integration is project-specific rather than inherently good or bad. Assess the effect on plant efficiency, network ΔT, hydraulic capacity and dispatch before selecting it.
Notes: The supply-versus-return connection explanation is too simple. Return-line integration can increase return temperatures and reduce generation efficiency; suitability depends on temperatures, hydraulics, network configuration and the displaced generation.

## Slide 9
When storage supports recovered-heat integration
Storage can help when:
source output varies;
heat demand occurs later than source availability;
the source has a minimum stable operating level;
heat-pump operation should be shifted;
short-term network constraints limit immediate export.
Monitor:
charging and discharging power;
storage temperatures;
state of charge;
standing losses;
source curtailment;
backup heat use.
Storage shifts heat in time. It does not solve insufficient annual energy, unsuitable temperature or long-term source unreliability.

## Slide 10
Initial surplus-heat screening matrix
Criterion | Questions to ask
Temperature | Minimum, normal and maximum source temperature?
Capacity | Recoverable kW or MW? Annual MWh?
Availability | Hours per day, days per year and seasonal pattern?
Demand match | Is network demand present when the source operates?
Distance | Pipe length, route and elevation?
Reliability | Planned shutdowns, process variability and expected site lifetime?
Heat quality | Clean water, contaminated water, air or process gas?
Integration need | Heat exchanger, heat pump, storage or backup?
Carbon benefit | Which existing heat source will be displaced?
Commercial interface | Ownership, pricing, guarantees and maintenance responsibility?
Economic potential | Calculate the technically recoverable and usable heat, then assess whether its recovery is economically viable.

## Slide 11
Where can industrial surplus heat be found?
Potential sectors include:
steel and non-ferrous metals;
cement, glass and ceramics;
refineries and chemicals;
food and beverage processing;
pulp and paper;
textiles;
refrigeration and cold storage;
manufacturing cooling-water systems;
compressors and compressed-air systems;
industrial wastewater.
Source forms
flue gas;
cooling water;
hot product or process streams;
condensate;
exhaust air;
refrigeration condenser heat.
Notes: Not all industrial sources are high-temperature or suitable for direct supply-line integration

## Slide 12
Typical strengths and limitations of industrial sources
Possible strengths
high thermal capacity;
long operating hours;
relatively stable output;
existing heat-rejection systems;
potentially useful temperatures.
Possible limitations
process shutdowns;
fluctuating production;
contaminated or corrosive fluids;
fouling and scaling;
distance from the network;
source-site closure risk;
industrial production takes priority over heat export.

## Slide 13
Common urban surplus-heat sources
Potential sectors include:
data centres;
supermarket and cold-store refrigeration;
commercial-building cooling systems;
wastewater and treated sewage;
metro and rail ventilation;
hospitals and laboratories;
ice rinks and leisure centres;
power and telecommunications infrastructure.
Typical characteristics:
low or medium temperature;
distributed locations;
strong dependence on heat pumps;
relatively close to urban heat demand;
potential for year-round operation.

## Slide 14
Data-centre heat reuse
Heat may be recovered from:
air-based cooling systems;
chilled-water circuits;
direct liquid cooling;
immersion-cooling systems.
Key screening questions
What temperature is available?
Is the cooling load stable throughout the year?
Is a heat pump required?
Is the heat-network connection close enough?
Can the data centre reject heat independently if the network is unavailable?
Who owns and operates the recovery equipment?
How will source availability be guaranteed?
Main principle
The district-heating connection must never compromise data-centre cooling or server availability.
Notes: recovery temperature depends strongly on the cooling architecture

## Slide 15
Wastewater heat recovery
Wastewater can provide a comparatively stable low-temperature source.
Possible recovery locations include:
building sewer connections;
main sewers;
wastewater-treatment plants;
treated effluent discharge.
A typical system includes:
wastewater or effluent heat exchanger;
cleaning or fouling-control system;
heat pump;
pumps and controls;
backup heat source.
Key risks
fouling and blockage;
corrosion;
variable wastewater flow;
maintenance access;
hygiene separation;
permitted minimum discharge temperature.

## Slide 16
Normal operation or possible fault?
Possible warning patterns
source available but no heat exported;
export command active but no flow;
high flow with little transferred heat;
heat pump running with low thermal output;
unstable export temperature;
frequent start/stop cycling;
storage charging and discharging simultaneously;
source curtailed while backup heat is operating.
First checks
confirm operating mode;
review source-availability signal;
compare command and equipment response;
check temperatures on both sides of the heat exchanger;
verify flow direction;
confirm whether storage is charging or discharging.
A pattern is abnormal only when it differs from the approved control sequence.

## Slide 17
What should the monitoring system show?
Source availability
available/not available;
maximum recoverable power;
planned shutdowns.
Delivered heat
thermal power;
energy;
source and delivery temperatures;
flow rate.
Conversion equipment
heat-pump electrical input;
heat output;
COP;
start count and run hours.
Network response
supply and return temperatures;
pressure and flow;
backup-generation output;
storage state of charge.
Environmental reporting
displaced heat source;
electricity used for recovery;
calculated emissions impact;
method and assumptions.
Carbon benefit should be calculated using an agreed methodology—not inferred from heat-meter data alone.
Notes: Smart meters do not directly establish “specific CO₂ savings” without a defined baseline and emissions-accounting method.

## Slide 18
Applied case: data-centre heat for an urban network
Source
source-side recoverable heat: 2 MW
source temperature: 30°C
availability: 24 hours/day
network supply/return: 70/40°C
connection distance: 800 m
Proposed arrangement
source-side heat exchanger;
large heat pump;
supply-line connection;
short-term thermal storage;
independent data-centre heat rejection.
Questions
Can the heat be used directly?
Why is a heat pump required?
What data are needed to estimate COP and annual delivery?
What happens when network demand is low?
Which party must maintain backup heat rejection?
What evidence is needed before approving the project?
Notes: Expected conclusion
direct supply is not possible at 30°C;
heat-pump boosting is required;
annual source profile and network demand must be compared;
storage may reduce short-term mismatch but not seasonal surplus;
data-centre cooling must remain independent;
detailed hydraulic, electrical, commercial and carbon assessments are required.

## Slide 19
Five rules for recovered-heat integration
Reduce and reuse heat on-site first. Export genuinely available surplus heat.
Screen the source before selecting equipment. Temperature, capacity, timing, distance and reliability determine viability.
Choose the connection for the whole system. Direct use, heat-pump boosting, return-line integration and storage have different effects.
Protect both primary activities. The source process and the heat network require backup and fail-safe operation.
Measure availability and delivered performance. Temperatures, flow, power, equipment status and operating mode must support commercial and technical verification.

## Slide 20
www.repowerregions.eu
Follow our journey