Building interface and metering check

Identify and inspect a heat interface, and verify the meter reading is plausible

| Time needed | Approximately 4 hours: 2 hours on site, 2 hours completing the record |
| --- | --- |
| Where | A building substation or heat interface unit you can access with your supervisor |
| Supervision | A competent supervisor must be present for the whole site visit |
| You produce | A completed interface and metering record |
| Works with | EQF 4 Modules 3, 5 and 6; CVET Module 4 Unit 2 |

What you will be able to do

- Identify whether a building connection is direct or indirect.

- Recognise the main components of a heat interface and say what each does.

- Read a heat meter and record the values it reports.

- Judge whether those readings are plausible for the operating conditions at the time.

- Recognise what must be escalated rather than handled yourself.

The task

1.  Agree the site with your supervisor and confirm access permission and site rules.

2.  Before you go, ask for the approved schematic or record drawing. Do not assume what is inside the unit — check the drawing.

3.  Identify the connection type. Is the building connected directly to the network, or indirectly through a heat exchanger? Record how you can tell.

4.  Identify the components you can see, and note what each one is for. Do not open anything to look inside.

5.  Record the meter identification: the meter ID, what boundary it measures, and whether it matches the drawing or record.

6.  Inspect visually: is the flow arrow pointing the right way, are sensors in the correct pipes, is the unit accessible and free of leaks, are seals and identification intact.

7.  Read the display and record the values available, with their units.

8.  Carry out the plausibility check using the table on the next page. Note the operating conditions at the time — a reading is only plausible or not in relation to what the system is doing.

9.  Record anything that should be escalated. You are not expected to fix anything.

10.  Complete the record and discuss it with your supervisor.

Interface record

| What to record | Your answer |
| --- | --- |
| Site and building |  |
| Date and time of visit |  |
| Connection type: direct or indirect |  |
| How you identified the connection type |  |
| Approved schematic available? Does it match what you see? |  |
| Components identified (list what you can see) |  |
| Meter ID / serial number |  |
| What boundary does this meter measure? |  |
| Does the meter match the drawing or record? |  |
| Flow arrow direction correct? |  |
| Sensors appear to be in the correct pipes? |  |
| Unit accessible and free of visible leaks? |  |
| Seals and identification intact? |  |
| Communication indicator present and active? |  |

Meter readings

| Value | Reading | Unit |
| --- | --- | --- |
| Cumulative energy |  |  |
| Current power |  |  |
| Flow rate |  |  |
| Supply temperature |  |  |
| Return temperature |  |  |
| Temperature difference (ΔT) |  |  |
| Cumulative volume |  |  |

Plausibility check

First record what the system is doing. Then check the readings against it.

| Question | Your answer |
| --- | --- |
| Is there active heating demand at the time of the visit? |  |
| During active demand, is flow above zero? |  |
| Is supply temperature higher than return temperature? |  |
| Is power positive? |  |
| Did the energy register increase while you watched? |  |
| Any zero flow during confirmed demand? |  |
| Any unexpected flow when demand is off? |  |
| Do supply and return appear reversed? |  |
| Overall: are the readings plausible? Say why. |  |

Escalation record

Record anything you noticed that should be passed to a competent person. It is correct to record something you are unsure about.

| What you observed | Why it should be escalated | Who you reported it to |
| --- | --- | --- |

Important

This check verifies installation and plausibility. It does not recalibrate the meter and it is not a substitute for certified metrology. Do not check only whether the display is switched on. The point of this task is to check the complete measuring system: the right meter, at the right boundary, installed the right way round, giving readings that make sense.

How your work will be assessed

| Criterion | What good looks like |
| --- | --- |
| Safe working | You stayed within the visual and documentary scope throughout. |
| Correct identification | Connection type and components correctly identified, with reasoning. |
| Accurate recording | Readings recorded with correct units and the operating conditions noted. |
| Plausibility judgement | You related the readings to what the system was actually doing. |
| Escalation | You recognised what is not yours to resolve. |
| Completeness | Gaps are marked as such rather than left blank. |

Supervisor sign-off

To be completed by the workplace supervisor. The learner cannot be assessed on this project without a completed sign-off.

| Item | Supervisor confirmation |
| --- | --- |
| Site agreed, access permission and site rules confirmed |  |
| Supervisor present for the whole visit |  |
| Learner remained within the visual and documentary scope |  |
| Record completed and discussed |  |
| Any escalations passed to the responsible person |  |

| Supervisor name |  |
| --- | --- |
| Role / organisation |  |
| Signature |  |
| Date |  |
| Learner name |  |
| Learner signature |  |
| Date |  |