Surplus heat source screening

Assess whether a real local site could supply heat to a network

| Time needed | Approximately 6 hours: 2 hours desk research, 2 hours site contact or visit, 2 hours writing |
| --- | --- |
| Where | A local industrial, commercial or urban site. A site visit is useful but not essential. |
| Supervision | Workplace supervisor agrees the site and signs off the completed screening |
| You produce | A completed screening matrix and a short feasibility opinion |
| Works with | EQF 4 Modules 1, 5 and 7; CVET Module 4 Unit 5; mapping tool VET-05 |

What you will be able to do

- Recognise where surplus heat is likely to be found in your local area.

- Apply a structured screening method rather than judging by impression.

- Identify whether a source is hot enough for direct use or would need a heat pump.

- Recognise that availability and demand match matter as much as temperature and quantity.

- Form and justify an early feasibility opinion.

Before you start

Desk research first Find out what the site does before you contact anyone. You will ask better questions and you will be taken more seriously. If you arrange a visit, go with your supervisor and follow the site's access rules. Much of this task can be completed without entering the site at all. Do not approach a site without your supervisor's agreement. You are representing your organisation.

Choosing a site

Potential sectors include steel and non-ferrous metals, cement, glass and ceramics, refineries and chemicals, food and beverage processing, pulp and paper, and textiles. Urban sources include data centres, wastewater treatment, supermarkets, ice rinks, metro systems and commercial cooling.

Choose somewhere real and local. A modest, genuine site produces a better piece of work than an impressive one you cannot find anything out about.

The task

1.  Agree a site with your supervisor.

2.  Desk research: what does the site do, what processes run there, what are the operating hours, and is there any published information about its energy use?

3.  Identify where heat is currently rejected. Cooling towers, flue gases, condensers, wastewater, ventilation exhaust.

4.  Work through the screening matrix on the next page. Record 'unknown' where you cannot find out — that is a real and useful finding at screening stage.

5.  Decide whether the source temperature would allow direct transfer through a heat exchanger, or whether a heat pump would be needed to raise it.

6.  Consider where the heat could go. Is there a network nearby? Use the Peta4 mapping tool (VET-05) to check heat demand density in the area.

7.  Form a feasibility opinion: worth investigating further, not worth investigating, or cannot tell without more information. Any of the three is a valid answer if you justify it.

8.  Write up your opinion in roughly 400–600 words.

Screening matrix

Adapted from the initial surplus-heat screening matrix, CVET Module 4 Unit 5.

| Criterion | Questions to ask | Your findings |
| --- | --- | --- |
| Temperature | Minimum, normal and maximum source temperature? |  |
| Capacity | Recoverable kW or MW? Annual MWh? |  |
| Availability | Hours per day, days per year and seasonal pattern? |  |
| Demand match | Is network demand present when the source operates? |  |
| Distance | Pipe length, route and elevation? |  |
| Reliability | Planned shutdowns, process variability and expected site lifetime? |  |
| Heat quality | Clean water, contaminated water, air or process gas? |  |
| Integration need | Heat exchanger, heat pump, storage or backup? |  |
| Carbon benefit | Which existing heat source would be displaced? |  |
| Commercial interface | Ownership, pricing, guarantees and maintenance responsibility? |  |
| Economic potential | Is recovery likely to be economically viable? |  |

Your feasibility opinion should cover

- What the site is and what heat it rejects.

- Whether the temperature would allow direct use or would need a heat pump, and why.

- Whether the heat is available when it would be needed.

- What you could not find out, and what you would need to ask next.

- Your conclusion: worth investigating further, not worth it, or cannot tell yet.

How your work will be assessed

| Criterion | What good looks like |
| --- | --- |
| Site choice | A real, local, plausible site with a genuine heat rejection route. |
| Use of the matrix | All eleven criteria addressed, with gaps marked as unknown rather than guessed. |
| Temperature reasoning | You reached a clear view on direct use versus heat pump, and justified it. |
| Demand match | You considered timing, not only quantity. |
| Honest conclusion | Your opinion follows from your findings, including where those findings were thin. |
| Next questions | You identified what you would need to ask to take it further. |

A note on what screening is for

Screening is not a feasibility study. It is a first filter. A good screening result can be negative. Establishing early that a source is unsuitable saves far more than pursuing one that was never going to work. 'Not worth investigating, and here is why' is a complete and valuable answer.

Supervisor sign-off

To be completed by the workplace supervisor. The learner cannot be assessed on this project without a completed sign-off.

| Item | Supervisor confirmation |
| --- | --- |
| Site agreed with supervisor |  |
| Any site contact or visit conducted appropriately |  |
| Screening matrix completed |  |
| Feasibility opinion submitted and discussed |  |
| Supervisor comments |  |

| Supervisor name |  |
| --- | --- |
| Role / organisation |  |
| Signature |  |
| Date |  |
| Learner name |  |
| Learner signature |  |
| Date |  |

RePower Regions — Sustainable Skills for Heating and Cooling Professionals  |  EQF Level 4  |  CC BY 4.0

Funded by the European Union. Views and opinions expressed are however those of the author(s) only and do not necessarily reflect those of the European Union or the European Education and Culture Executive Agency (EACEA). Neither the European Union nor EACEA can be held responsible for them.